## Sheet1
S.No. | Query raised | Global Energy Alliance Response
1 | Is this EOI for a single pilot DT site, or should applicants price and design for eventual multi-site rollout? Section 1.4 refers to "multiple DT sites in a phased manner" - how many sites are envisaged at pilot stage versus the eventual RFP? | A single Distribution Transformer site is considered for the pilot.
2 | Kindly share the specific DT location (or at minimum the feeder/circle) so applicants can assess site conditions, road access, and existing infrastructure. | The specific DT location will be shared at the RFP stage. All sites have road access and pre-built infrastructure.
3 | Is a site visit being arranged prior to the 22-Aug-2026 submission deadline, given the compressed timeline? | As this is an Expression of Interest, the assessment at this stage is of the technical feasibility of the proposed OEM's solution. A site visit can be arranged at the RFP stage.
4 | What is the existing DT capacity (kVA), present loading profile, and available space/land at the substation/DT premises for the BESS footprint? | The DT details, including capacity and present loading profile, will be shared at the RFP stage.
5 | Does the Client already have a prepared land/civil platform available, or is site preparation (foundation, boundary wall, access road) part of the bidder's scope of supply? | Land is under the Client's scope. Civil works are under the vendor's scope.
6 | Is grid-tied operation only expected, or is islanded/backup operation during grid outages also an intended use case? | The pilot is not intended for backup operation. The system will primarily be used for peak shaving to support utility peak loading.
7 | Given the 12-15 year design life, what performance warranty period does the Client expect bidders to offer? | A performance warranty period of 10 years is expected.
8 | For the requested SoH milestones (1/3/8/12 years), should degradation be modelled at the stated 550 cycles/year, or should bidders also show sensitivity at 2 cycles/day (~730 cycles/year) as referenced elsewhere for the DT-level use case? | Planning shall be done for two full cycles per day. Actual operation may be lower on an as-required basis. State of Health degradation shall be modelled on the two-cycle-per-day basis.
9 | Is there a minimum acceptable round-trip efficiency (DC or AC) for technical qualification, or is this purely an evaluation/comparison parameter with no floor? | No minimum round-trip efficiency threshold is prescribed. A higher efficiency figure is highly recommended and will be an important factor in vendor evaluation.
10 | Will the Client provide historical DT load curves and voltage profile data to support sizing of the power (kW) and duration (hours) configuration, or is sizing left entirely to bidder judgement? | A power requirement of 125 kW with a battery capacity of 250 kWh over a two-hour duration is recommended. In actual operation this may scale to a 60 kW power requirement over a four-hour window.
11 | Since AT&C loss reduction and voltage support are named objectives but no reactive power duty cycle is specified, is there an expected daily reactive power dispatch profile, or is real-power arbitrage/peak-shaving the primary duty? | Real-power arbitrage and peak shaving are the primary duty.
12 | Under which regulatory framework will this BESS be connected and operated - is it to be treated as a DISCOM asset requiring formal CEA/SERC approval, or as a private pilot asset operating behind the meter? | The BESS will eventually be treated as a DISCOM asset, and the applicable framework will follow DISCOM regulations.
13 | Who will own and operate the BESS post-commissioning? Is this envisaged as a straightforward capital-supply contract, a BOOT/BOO model, or does the O&M responsibility described in Section 2 imply the bidder retains long-term O&M for a fee under a separate arrangement? | It will not be BOO Model tentative expectation is of Two years of O&M is built into the scope of this project. The remaining eight years of operational life will be borne by the utility and will be contracted separately subject to change in RFP.
14 | What commercial/payment model is envisaged for the eventual RFP - outright capex sale, an Energy-as-a-Service/leasing structure, or performance-linked payments? This materially affects how bidders should structure their techno-commercial response. | Possible Commercial Model can be Outright capex sale with performance-linked payment.
15 | Will the BESS require metering and settlement approval from the State Electricity Regulatory Commission, and who bears responsibility for securing that approval - the Client or the bidder? | Obtaining the required approvals from the State Electricity Regulatory Commission is within the Client's scope.
16 | Since several referenced standards (e.g., UL 9540A, UL 1973) were developed for lithium-ion chemistries, will GEAPP/Client accept equivalent sodium-ion-specific certification where available, or is UL 9540A-type third-party testing mandatory even where it requires a bespoke test campaign for sodium-ion cells? | To ensure that best-quality cells are used, vendors will be evaluated on the basis of the highest level of testing demonstrated. Applicants shall state the applicable standard and its status, with remarks alongside.
17 | Are there specific BIS/CEA notifications applicable to sodium-ion BESS that the Client expects bidders to comply with, given that this chemistry is still emerging in the Indian regulatory context? | Sodium-ion remains an emerging technology in the Indian energy context. Equivalent technology such as lithium-ion may be used as a reference for benchmarking.
18 | Section 3 requests turnover, net worth and profit for FY 2023-24 through FY 2025-26 - is there a minimum financial eligibility threshold (e.g., minimum turnover or net worth) applicable at EOI stage, or is this purely informational? | No. There is no minimum financial eligibility threshold at the EOI stage.
19 | Does the Client have any concessional GST/customs duty benefit or scheme (analogous to ALMM-type provisions) applicable to sodium-ion BESS that bidders should factor into pricing? | No. No concessional GST or customs duty benefit or scheme is applicable.
20 | Regarding GEAPP's Profit Blocking Mechanism (Section 1.5.2) - does this apply to the entire capex plus O&M contract value, or only to a specific grant/subsidy component funded directly by GEAPP? Kindly clarify the overall funding structure - i.e., whether this is Client capex with GEAPP as technical facilitator, or a jointly funded pilot. | Under Discussion- Will be shared as a Part of RFP
21 | Since this EOI is explicitly a precursor to a separate RFP, will EOI respondents receive any pre-qualification weightage in the subsequent RFP, or will that process be fully open to new bidders as well? | This EOI is being used to understand OEM technical capabilities and the readiness of the solutions available. Subject to internal policy, GEAPP may proceed with a closed-structure RFP, which would be open for submission to vendors participating in this EOI.
22 | Given the EOI was released on 5-Aug-2026 and involves an emerging technology requiring OEM/vendor data coordination, can the question submission deadline of 14-Aug-2026 be extended by a reasonable period? | No. A separate RFP will be floated which will cover all questions and allow ample response time. Every effort will be made to hold an introductory call with vendors between EOI closure and the RFP issue date.
23 | Will responses to proposer questions (targeted 16-Aug-2026) be shared with all bidders on an anonymised, consolidated basis, or communicated individually to each respondent? | Responses will be communicated to each respondent. They will also form part of the separately floated RFP.
24 | Is a prescribed Excel-based BOQ/commercial template available, beyond the datasheet format in Section 5, that GEAPP can share to standardise commercial submissions across bidders? | For a like-for-like comparison between vendors, applicants are advised to use the format shared in the EOI.
25 | What is the exact DT rating (kVA), voltage (415 V confirmed?), vector group and configuration (3-phase, 4-wire) at the pilot site? Is a single DT or multiple DTs envisaged for the pilot? | The point of connection is the 415 V side of the distribution transformer. A single Distribution Transformer site is considered for the pilot. The DT details, including rating and configuration, will be shared at the RFP stage.
26 | Can the utility share at least one year of 15-minute (or hourly) load data for the pilot DT, including phase-wise loading, to size power and validate the two-cycle-per-day assumption? | The DT load data will be shared at the RFP stage.
27 | Should the 200-400 kWh be interpreted as usable AC energy at BOL at the point of connection, or as nameplate DC? Please confirm the measurement basis for all energy and SoH guarantees. | Usable energy capacity is to be taken as a minimum of 250 kWh. Where a particular sizing requires it, a capacity above 250 kWh may be considered.
28 | Is a preferred power rating, C-rate or peak-shaving target (kW reduction at the DT) defined, or is the bidder free to propose within the 2-4 hour band? | A power requirement of 125 kW with a battery capacity of 250 kWh over a two-hour duration is recommended. In actual operation this may scale to a 60 kW power requirement over a four-hour window.
29 | Is "up to two full cycles per day" a firm design duty or an upper bound? What average equivalent-full-cycles-per-day should be used as the warranty basis? | Planning shall be done for two full cycles per day. Actual operation may be lower on an as-required basis. State of Health degradation shall be modelled on the two-cycle-per-day basis.
30 | Given the stated 48-50 deg C ambient and passively cooled sodium-ion modules, is active thermal management (enclosure cooling) acceptable/expected, noting its parasitic-energy impact on round-trip-efficiency guarantees? | Accepted. Auxiliary energy and parasitic energy are to be treated as separate loss elements.
31 | Is the requirement strictly sodium-ion for the battery only, with freedom to pair any BMS-compatible PCS (including imported inverters)? Any restriction on imported power-conversion equipment? | No restriction. The sodium-ion requirement applies to the battery; there is no restriction on the power conversion system, including imported inverters.
32 | Given sodium-ion's nascency, will IEC 62619 + UN 38.3 + cell/module thermal-propagation testing be accepted in lieu of UL 9540A / UL 9540 where the latter is not yet available for the specific cell? What is the minimum mandatory certification set for the RFP stage? | To ensure that best-quality cells are used, vendors will be evaluated on the basis of the highest level of testing demonstrated. Applicants shall state the applicable standard and its status, with remarks alongside.
33 | Which interconnection standard applies at 415 V (CEA regulations / RERC / the utility's own DT-interconnection norms)? Are EU-certified inverters (IEC 62109, VDE-AR-N 4105, G99) acceptable subject to demonstrated Indian applicability? Is an isolation transformer mandated? | Not mandated, but highly recommended.
34 | Please confirm acceptable India-hosting options (on-premises at the utility, India-based cloud, or utility-SCADA integration) and any CEA cyber-security requirements for the servers and data. | Cloud storage will be provided by the utility. The required cyber-security measures shall be applied to the servers and the data at the server end.
35 | Does the bidder's scope include the 415 V interface switchgear, metering, protection relays and any DT-side modifications, or are these utility-provided? Please confirm the point-of-connection demarcation. | Applicants are requested to share tentative costing both including and excluding the 415 V interface switchgear, metering, protection relays and DT-side modifications.
36 | Will the utility provide the land/pad, foundation, boundary and power evacuation, or is civil work in the bidder's scope? Is there a space constraint at the pilot DT site? | Land is under the Client's scope. Civil works are under the vendor's scope. All sites have road access and pre-built infrastructure.
37 | What O&M period and SLA structure (availability %, response time, penalties) are expected? Is O&M mandatory within the same package or contracted separately? | Not finalized yet, tentatively take two years of O&M is built into the scope of this project. The remaining eight years of operational life will be borne by the utility and will be contracted separately. This info is bound to change.please refer future RFP for finalized status.
38 | Under the RFP, will procurement be turnkey capex or an availability/performance-linked model? Is there any VGF/GEAPP funding structure affecting pricing, and how does the Profit-Blocking Mechanism apply to a commercial supplier's normal margin? | Procurement will be an outright capex sale with performance-linked payment.
39 | Is planned augmentation over the 12-year life acceptable, or must the system meet the energy guarantee without augmentation? Who bears augmentation cost - supplier or utility? | lanned augmentation over the project life is acceptable. Applicants are requested to provide costing for both options — with planned augmentation and without augmentation — so that the two can be compared.
40 | Is there a committed pipeline (MWh / 10 MWh) beyond the pilot, and an indicative timeline/quantity for phased scale-up, so bidders can reflect volume-based cost reduction? | A single Distribution Transformer site is considered for the pilot.
41 | Please confirm the required performance-warranty horizon (12 vs 15 years) and whether it must be measured at the AC point of connection inclusive of auxiliaries. | A performance warranty period of 10 years is expected.
42 | The EOI is governed by the laws of the State of New York. Will the eventual RFP/contract for an Indian DT deployment be executed under Indian law and jurisdiction? | As GEAPP is carrying a sponsorship role, the applicable law will be handled as per GEAPP's internal mandate, which is the law of the State of New York.
43 | Site & scale: can we get DT's load profile, phase-imbalance and voltage data? Is this a single pilot DT or a phased rollout across multiple sites? | The DT load profile, phase-imbalance and voltage data will be shared as part of the RFP. A single Distribution Transformer site is considered for the pilot.
44 | Configuration: Is there a preferred kW rating / discharge duration and a fixed capacity target, or is sizing fully open? | A preferred rating applies. Applicants may propose variation above the preferred rating.
45 | Phase control: Is independent per-phase (four-wire) power control mandatory, or desirable only, at the EOI stage? | Phase unbalance is to be considered as 100%. The proposed system shall be designed on that basis.
46 | Certification: For sodium-ion, are UL 9540A / UL 1973 (or equivalents) required at this stage, or is an 'under certification' status acceptable? | UL 9540A / UL 1973 or equivalents are highly recommended. Where a standard is under certification, the applicant shall mark it as a deviation and provide an appropriate timeline for completion. Where a cited standard was originally developed for lithium-ion or another battery chemistry, the applicant shall demonstrate its applicability to the proposed sodium-ion product.
47 | Scope & RFP: What is the anticipated Client-versus-vendor split for land, civil works Will the forthcoming RFP be drawn only from the EOI shortlist, and when is it expected? | Land is under the Client's scope. Civil works are under the vendor's scope. This EOI is being used to understand OEM technical capabilities and the readiness of the solutions available. Subject to internal policy, GEAPP may proceed with a closed-structure RFP, which would be open for submission to vendors participating in this EOI.
48 | Additionally, we would welcome the opportunity to arrange a site visit to the proposed DT location, or to receive available site data, to support accurate technical sizing in our Proposal. | As this is an Expression of Interest, the assessment at this stage is of the technical feasibility of the proposed OEM's solution. A site visit can be arranged at the RFP stage.
49 | Energy basis — whether the stated energy is usable AC at the point of connection or nameplate DC, and the measurement basis for all energy and SoH guarantees | The specified energy capacity shall be considered as usable energy, with a minimum usable capacity of 250 kWh. Applicants shall clearly state the DC nameplate capacity, usable battery-side energy, and usable AC energy at the point of connection. The final measurement methodology for energy and State of Health guarantees will be specified in the RFP. Auxiliary and parasitic energy consumption shall be separately identified.
50 | Thermal management — whether active enclosure cooling is acceptable given the 48–50°C site ambient, and how its parasitic load should be treated in round-trip-efficiency guarantees | Active enclosure cooling is acceptable. Energy consumed by the thermal-management system and other auxiliary systems shall be separately identified as auxiliary or parasitic consumption. Applicants shall clearly state whether the quoted round-trip efficiency is inclusive or exclusive of these loads. The final performance measurement methodology will be specified in the RFP.
51 | Certification — whether IEC 62619 + UN 38.3 together with cell/module thermal-propagation testing will be accepted where UL 9540A / UL 9540 is not yet available for the specific sodium-ion cell. | Applicants shall provide details of all applicable certifications and test reports available for the proposed sodium-ion technology, including IEC 62619, UN 38.3, and cell/module thermal-propagation testing, where applicable. UL 9540A, UL 9540, UL 1973, or equivalent certifications are highly recommended. Where a certification is unavailable or under progress, the applicant shall identify it as a deviation, provide the current status, and indicate the expected timeline for completion. Vendors will be evaluated based on the highest level of testing and safety assurance demonstrated.
52 | Existing Electrical Distribution Board: Please confirm whether the BESS power connection will be made to the purchaser's existing electrical distribution board, or whether a new/modified board is also required to be considered in our scope. | The final connection arrangement and the requirement for a new or modified electrical distribution board will be confirmed at the RFP stage based on the selected site. At the EOI stage, applicants are requested to provide tentative costing for both scenarios: connection to the existing electrical distribution board and provision or modification of the required board, switchgear, protection, and associated interface equipment.
53 | Panel Supply and Installation Location: If the panel is to be supplied by us, please provide the proposed installation location. | The proposed panel installation location and site layout will be shared at the RFP stage along with the detailed site information. Where a new panel is required, its supply, installation, cabling, protection, testing, and commissioning shall be considered in the applicant's tentative costing as a separately identified item.
54 | Battery Container Installation: Please confirm whether the battery container will be installed inside an existing room/building, or whether we are required to consider the construction of a suitable foundation and shed for the container. | The BESS will be deployed at an open site and will not be installed inside an existing room or building. Land will be provided by the Client. The vendor shall consider the required foundation, shed or weather-protection structure, and associated civil works within its scope. Detailed site and civil-work requirements will be provided in the RFP.
55 | Distance Between Container and Control Room/Panel: Please provide the approximate distance between the battery container and the control room, where the new panel or existing panel is proposed to be installed. | The approximate distance between the battery container and the control room or electrical panel will be shared at the RFP stage along with the proposed site layout and other site details. Applicants may state their assumptions for preliminary cable sizing and costing at the EOI stage.
56 | Power Utilization: Please confirm whether the BESS power will be exported to the grid or utilized for behind-the-meter applications only. | The primary purpose of the project is to demonstrate peak-load shaving at the Distribution Transformer level. The BESS will be connected to the 415 V side of the Distribution Transformer and will discharge to reduce peak loading on the transformer. The pilot is not intended primarily for backup or islanded operation. Detailed operating and power-flow requirements will be specified in the RFP.
57 | Metering Requirement: Please confirm whether main and check meters are required for both import and export metering purposes. | The required meters will be provided by the utility. The detailed metering arrangement, including whether main and check meters are required for import and export measurement, will be confirmed in the RFP.
58 | Black Start Capability: Please confirm whether the proposed PCS is required to have black start capability. | Black start capability is not mandatory, as the pilot is not intended for islanded or backup operation. The primary operating requirement is grid-connected peak shaving at the Distribution Transformer level. Applicants may indicate black start capability as an optional feature, where available, and provide its associated cost separately.